## Instructions
3-phase Capacity Planning Tool - INSTRUCTIONS
Welcome to the Raritan 3-phase capacity planning tool. These vendor-agnostic spreadsheets aim to demystify the process of correctly loading 3-phase rack power strips -- to ensure maximum power capacity while preventing overloading.
1 | You will find five power strip capacities below (worksheet tabs). It is critically important to utilize correct planning tool sized for your rack power strip. Consult the spec sheet or engineering submittals of your rack power strip, to determine the rated input current -- not just the input plug type.
2 | For each outlet type (C13 or C19), per breaker -- enter in expected loads and, optionally, the name of the device drawing the load. For Tier II (and above) redundancy situations, complete the spreadsheet assuming that the other (redundant) power strip in the cabinet is offline.
3 | The capacity planning tool will automatically highlight any error conditions. So long as the field "capacity check" in the bottom-righ of the spreadsheet reads "OK" (Green), your rack power strip has not exceeded its capacity constraints.
BE CAREFUL to choose the correct power strip capacity worksheet:
60A plug | Note that rack power strip vendors provide multiple products with 60A plugs (IEC 60309 60A 3P4W), but with two different rated currents: either 48A or 45A. (This is because 45A units only require smaller, 6# AWG cable -- not 4# AWG). Be sure to select the correct worksheet that corresponds to your power strip.
50A plug | Note that rack power strip vendors provide products with 50A plugs (Hubbell CS8365C, "California Style"), but with two different rated currents: either 40A or 35A. (This is because 35A units only require 3 branch circuit breakers -- not 6). Be sure to select the correct worksheet that corresponds to your power strip.
© 2011 Raritan Inc. - by Michael Suchoff and Henry Hsu

## 30A (24A ¦ 8.6kVA)
© 2011 Raritan Inc. by Michael Suchoff & Henry Hsu
3-phase Capacity Planning Worksheet - 208V // 30A (24A) per line
L1/L2 [XY] | [5 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Current by Breaker
[19 empty] | A | 8.1
[19 empty] | B | 10.6
| Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | C | 11.5
| Circuit Breaker A (L1/L2) | [5 empty] | Circuit Breaker B (L2/L3) | [5 empty] | Circuit Breaker C (L3/L1) | [5 empty] | no breaker > 20A
| C13 | ExchangeServer EAST |  | 1.3 | 270.4 |  | C13 | SAP AppSvr 1of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 1of5 |  | 1.2 | 249.6 |  | OK
| C13 | ExchangeServer WEST |  | 1.3 | 270.4 |  | C13 | SAP AppSvr 2of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 2of5 |  | 1.2 | 249.6
| C13 | [5 empty] | C13 | SAP AppSvr 3of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 3of5 |  | 1.2 | 249.6 |  | Current by Line Pair
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 4of5 |  | 1.2 | 249.6 |  | L1/L2 | 8.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 5of5 |  | 1.2 | 249.6 |  | L2/L3 | 10.6
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L3/L1 | 11.5
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | maximize capacity by loading @ ~13.8A / pair
| C13 | [5 empty] | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | Phase Balance
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L1 | 97.58%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L2 | 92.91%
| C19 | UCS Chassis PS1 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS2 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS3 |  | 5.5 | 1144 |  | L3 | 109.5%
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | maximize capacity by balancing load
| C19 | [5 empty] | C19 | [5 empty] | C19
| C19 | [5 empty] | C19 | [5 empty] | C19
| C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | Capacity Remaining
|  | OK | [5 empty] | OK | [5 empty] | OK |  |  |  |  | L1 | 28.92%
[19 empty] | L2 | 32.32%
[19 empty] | L3 | 20.23%
| 17.0585 |  | 16.2428 |  |  | 19.1443 |  |  | 6.2816 | [5 empty] | OK
| L1 Current (A) |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 24A |  | cannot exceed 24A |  |  | cannot exceed 24A |  |  | will not exceed 8.6kVA | [8 empty] | version 2

## 50A (35A ¦ 12.6kVA)
© 2011 Raritan Inc. by Michael Suchoff & Henry Hsu
3-phase Capacity Planning Worksheet - 208V // 50A (35A) per line
L1/L2 [XY] | [5 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ]
For 35A power strips, simply ensure that no breaker exceeds 20A
| Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA
| Circuit Breaker A (L1/L2) | [5 empty] | Circuit Breaker B (L2/L3) | [5 empty] | Circuit Breaker C (L3/L1)
| C13 | ExchangeServer EAST |  | 1.3 | 270.4 |  | C13 | SAP AppSvr 1of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 1of5 |  | 1.2 | 249.6
| C13 | ExchangeServer WEST |  | 1.3 | 270.4 |  | C13 | SAP AppSvr 2of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 2of5 |  | 1.2 | 249.6 |  | Current by Breaker
| C13 | [5 empty] | C13 | SAP AppSvr 3of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 3of5 |  | 1.2 | 249.6 |  | A | 8.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 4of5 |  | 1.2 | 249.6 |  | B | 10.6
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 5of5 |  | 1.2 | 249.6 |  | C | 11.5
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | no breaker > 20A
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | OK
| C13 | [5 empty] | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | Phase Balance
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L1 | 97.58%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L2 | 92.91%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L3 | 109.5%
| C19 | UCS Chassis PS1 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS2 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS3 |  | 5.5 | 1144
| C19 | [5 empty] | C19 | [5 empty] | C19
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | Capacity Remaining
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | L1 | 51.26%
| C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | L2 | 53.59%
|  | OK | [5 empty] | OK | [5 empty] | OK |  |  |  |  | L3 | 45.3%
| 17.0585 |  | 16.2428 |  |  | 19.1443 |  |  | 6.2816 | [5 empty] | OK
| L1 Current (A) |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
version 2

## 50A (40A ¦ 14.4kVA)
© 2011 Raritan Inc. by Michael Suchoff and Henry Hsu; v2
3-phase Capacity Planning Worksheet - 208V // 50A (40A) per line
L1/L2 [XY] | [5 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Current by Breaker |  | no breaker to exceed 20A
[19 empty] | A | 6.75
[19 empty] | B | 1.25
| Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | C | 5.5
| Circuit Breaker A (L1/L2) | [5 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | D | 5.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 1of5 |  | 1.2 | 249.6 |  | E | 9.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 2of5 |  | 1.2 | 249.6 |  | F | 2.4
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 3of5 |  | 1.2 | 249.6 |  | OK
| C13 | ExchangeServer WEST |  | 1.25 | 260 |  | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | Current by Line Pair
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L1/L2 | 8
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | L2/L3 | 10.6
| C19 | UCS Chassis PS1 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS2 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS3 |  | 5.5 | 1144 |  | L3/L1 | 11.5
maximize capacity by loading @ ~23A / pair
| Circuit Breaker B (L1/L2) | [5 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 4of5 |  | 1.2 | 249.6
| C13 | [5 empty] | C13 | SAP AppSvr 1of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 5of5 |  | 1.2 | 249.6 |  | Phase Balance
| C13 | ExchangeServer EAST |  | 1.25 | 260 |  | C13 | SAP AppSvr 2of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L1 | 97.42%
| C13 | [5 empty] | C13 | SAP AppSvr 3of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L2 | 92.73%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L3 | 109.9%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | maximize capacity by balancing load
| C19 | [5 empty] | C19 | [5 empty] | C19
| C19 | [5 empty] | C19 | [5 empty] | C19
| C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | Capacity Remaining
|  | OK | [5 empty] | OK | [5 empty] | OK |  |  |  |  | L1 | 57.56%
[19 empty] | L2 | 59.6%
[19 empty] | L3 | 52.14%
| 16.9774 |  | 16.1604 |  |  | 19.1443 |  |  | 6.2608 | [5 empty] | OK
| L1 Current (A) |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 40A |  | cannot exceed 40A |  |  | cannot exceed 40A |  |  | will not exceed 14.4kVA

## 60A (45A ¦ 16.2kVA)
© 2011 Raritan Inc. by Michael Suchoff and Henry Hsu; v2
3-phase Capacity Planning Worksheet - 208V // 60A (45A) per line
L1/L2 [XY] | [5 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Current by Breaker |  | no breaker to exceed 20A
[19 empty] | A | 6.75
[19 empty] | B | 1.25
| Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | C | 5.5
| Circuit Breaker A (L1/L2) | [5 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | D | 5.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 1of5 |  | 1.2 | 249.6 |  | E | 9.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 2of5 |  | 1.2 | 249.6 |  | F | 2.4
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 3of5 |  | 1.2 | 249.6 |  | OK
| C13 | ExchangeServer WEST |  | 1.25 | 260 |  | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | Current by Line Pair
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L1/L2 | 8
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | L2/L3 | 10.6
| C19 | UCS Chassis PS1 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS2 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS3 |  | 5.5 | 1144 |  | L3/L1 | 11.5
maximize capacity by loading @ ~25.9A / pair
| Circuit Breaker B (L1/L2) | [5 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 4of5 |  | 1.2 | 249.6
| C13 | [5 empty] | C13 | SAP AppSvr 1of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 5of5 |  | 1.2 | 249.6 |  | Phase Balance
| C13 | ExchangeServer EAST |  | 1.25 | 260 |  | C13 | SAP AppSvr 2of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L1 | 97.42%
| C13 | [5 empty] | C13 | SAP AppSvr 3of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L2 | 92.73%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L3 | 109.9%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | maximize capacity by balancing load
| C19 | [5 empty] | C19 | [5 empty] | C19
| C19 | [5 empty] | C19 | [5 empty] | C19
| C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | Capacity Remaining
|  | OK | [5 empty] | OK | [5 empty] | OK |  |  |  |  | L1 | 57.56%
[19 empty] | L2 | 64.09%
[19 empty] | L3 | 57.46%
| 16.9774 |  | 16.1604 |  |  | 19.1443 |  |  | 6.2608 | [5 empty] | OK
| L1 Current (A) |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 45A |  | cannot exceed 45A |  |  | cannot exceed 45A |  |  | will not exceed 16.2kVA

## 60A (48A ¦ 17.3kVA)
© 2011 Raritan Inc. by Michael Suchoff and Henry Hsu; v2
3-phase Capacity Planning Worksheet - 208V // 60A (48A) per line
L1/L2 [XY] | [5 empty] | L2/L3 [YZ] | [5 empty] | L3/L1 [XZ] | [6 empty] | Current by Breaker |  | no breaker to exceed 20A
[19 empty] | A | 6.75
[19 empty] | B | 1.25
| Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | Type | Device Name |  | Amps | VA |  | C | 5.5
| Circuit Breaker A (L1/L2) | [5 empty] | Circuit Breaker C (L2/L3) | [5 empty] | Circuit Breaker E (L3/L1) | [5 empty] | D | 5.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 1of5 |  | 1.2 | 249.6 |  | E | 9.1
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 2of5 |  | 1.2 | 249.6 |  | F | 2.4
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 3of5 |  | 1.2 | 249.6 |  | OK
| C13 | ExchangeServer WEST |  | 1.25 | 260 |  | C13 | [5 empty] | C13
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | Current by Line Pair
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L1/L2 | 8
| C19 | [5 empty] | C19 | [5 empty] | C19 | [5 empty] | L2/L3 | 10.6
| C19 | UCS Chassis PS1 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS2 |  | 5.5 | 1144 |  | C19 | UCS Chassis PS3 |  | 5.5 | 1144 |  | L3/L1 | 11.5
maximize capacity by loading @ ~27.7A / pair
| Circuit Breaker B (L1/L2) | [5 empty] | Circuit Breaker D (L2/L3) | [5 empty] | Circuit Breaker F (L3/L1)
| C13 | [5 empty] | C13 | [5 empty] | C13 | CorpWebSvr 4of5 |  | 1.2 | 249.6
| C13 | [5 empty] | C13 | SAP AppSvr 1of3 |  | 1.7 | 353.6 |  | C13 | CorpWebSvr 5of5 |  | 1.2 | 249.6 |  | Phase Balance
| C13 | ExchangeServer EAST |  | 1.25 | 260 |  | C13 | SAP AppSvr 2of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L1 | 97.42%
| C13 | [5 empty] | C13 | SAP AppSvr 3of3 |  | 1.7 | 353.6 |  | C13 | [5 empty] | L2 | 92.73%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | L3 | 109.9%
| C13 | [5 empty] | C13 | [5 empty] | C13 | [5 empty] | maximize capacity by balancing load
| C19 | [5 empty] | C19 | [5 empty] | C19
| C19 | [5 empty] | C19 | [5 empty] | C19
| C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | C13 cannot exceed 12A; C19 cannot exceed 16A | [5 empty] | Capacity Remaining
|  | OK | [5 empty] | OK | [5 empty] | OK |  |  |  |  | L1 | 57.56%
[19 empty] | L2 | 66.33%
[19 empty] | L3 | 60.12%
| 16.9774 |  | 16.1604 |  |  | 19.1443 |  |  | 6.2608 | [5 empty] | OK
| L1 Current (A) |  | L2 Current (A) |  |  | L3 Current (A) |  |  | Total Power (kVA) | [5 empty] | Capacity Check
| cannot exceed 48A |  | cannot exceed 48A |  |  | cannot exceed 48A |  |  | will not exceed 17.3kVA